STATE OF OKLAHOMA

OFFICE OF THE STATE FIRE MARSHAL

Suppression System Plan Review Submittal Requirements

The following is a list of requirements for all plan submittals. Any information that is not provided may result in the plans being rejected and returned without review.

Application

- Completed Application Form with all fields filled-in.

Plans

- Two (2) sets of (paper) plans

Calculations

- Two (2) sets of (paper) calculations (if applicable)

Specifications

- One (1) set of specification book/books.

- One (1) CD containing all drawings, calculations, and specifications.

50% Walkthrough (if applicable) or 100% Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify the hood extends past the cooking appliance(s)

- Verify the proper backsplash is installed

- Verify all piping is properly secured

- Verify a fusible link is properly located

- Verify there is enough tension on the cable in order for the pull station to work properly

- Shut off valves for gas piping shall be prohibited in all non-accessible concealed locations and shut off valves shall be plainly marked, and visible from the floor, with an identification tag by the installer.  (IMC 1307)

- Verify all appliances are in place.  If the appliance is on wheels/rollers then a lanyard is required to be connected to the appliance and wall/floor.  The flooring must either be permanently marked identifying the exact location of all individual appliances or a device that will secure the legs/wheels of the individual appliance in place in order for the suppression nozzle to operate properly.

- Verify all nozzles are correctly placed in relation to the appliance

- Verify nozzles are installed to protect the hood horizontally and vertically

- Verify the gas is operational

- Verify the electric is operational

- Verify the hood is opertional

- Verify the pull station to each system is located between 10’ and 20’ of the appliance(s)

- If multiple hoods are installed, verify each system is properly labeled on the hood system and near the pull station

- Verify a Type K extinguisher is installed within 30’ of the appliances towards the exit

- Perform two tests: (1) cut a test link, (2) pull the pull station.  At least one test shall involve the blowing up of the balloons on all the nozzles

- Once the tests have been performed, verify the nozzles are taken off and checked for debris

- If a fire alarm system is installed verify it is tied to the fire alarm system

- If there is not a fire alarm system installed, provide a horn/strobe in the area where it can be seen throughout

- Verify the appropriate tag is placed on the riser with the correct information (if applicable)

- Verify a green tag is placed on the fire alarm control panel