STATE OF OKLAHOMA

OFFICE OF THE STATE FIRE MARSHAL

Carbon Monoxide Plan Review Submittal Requirements

The following is a list of requirements for all plan submittals. Any information that is not provided may result in the plans being rejected and returned without review.

Application

- Completed Application Form with all fields filled-in.

  - Fire Alarm

  - Carbon Monoxide

Plans

- Two (2) sets of (paper) plans

- Plans must be original plans with carbon monoxide devices only

- Plans must be drawn and printed to a scale no smaller than 1/8”

Calculations

- Two (2) sets of (paper) calculations

- Two (2) sets of (paper) voltage drop calculations

Specifications

- One (1) set of specification book/books.

- One (1) CD containing all drawings, calculations, and specifications.

50% Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify wiring is strapped up

- Verify notification device back boxes are installed as per the reviewed plans

- Verify initiating device back boxes are installed as per the reviewed plans

Final Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify a record of completion is filled out prior to the test

- Verify all devices are installed

- Verify a remote annunciator is located within 10’ of the main entrance

- Verify all carbon monoxide detectors are at least 3’ from all diffusers

- Verify all carbon monoxide are at least 3’ from the tip of all ceiling fan blades

- Test the duct detector with smoke for functionality.  A magnet only test the mechanism

- Verify the breaker associated with the carbon monoxide system is labeled in red

- Verify the electrical panel and breaker is identified in/on the carbon monoxide panel

- Verify the location of the electrical room is identified in/on the carbon monoxide panel

- Shut the breaker off to the carbon monoxide panel, should have an AC Loss

- Disconnect the battery terminal, show battery loss

- Shut the power off to the carbon monoxide control panel at least 24 hours in advance

- Verify the power is shut off to the carbon monoxide control panel

- Perform a function test for 5 minutes

- Verify the carbon monoxide control room is properly identified.

- Verify a map showing the location of the carbon monoxide control panel, power supply,

fuel-burning appliances, fuel-burning fireplaces, and forced-air furnaces

- Verify the appropriate tag is placed on the fire alarm control panel with the correct information

- Verify a green tag is placed on the fire alarm control panel