Oklahoma State Fire Marshal’s Office

Official Interpretation and Code Directive 2013-5

Fire Alarm System Requirements for Shunting Visual and/or Audio Distractions in Existing Buildings and/or Remodels of Existing Buildings

Effective June 1, 2013 (Revised 2-12-2018)

The guidelines set forth through the codes adopted by the Oklahoma Uniform Building Code Commission (OUBCC) and enforced by the Oklahoma State Fire Marshals Office can help to establish the requirements for an addition and/or remodels taking place.  This directive is to help simplify and bring clarity as to what is required to be installed.

Any addition and/or remodel to an Assembly, Education, and Special Amusement Building, must adhere to the current requirements to the adopted International Building Code (IBC), International Fire Code (IFC), and the Life Safety Code 101 as it relates to remodels.

A special amusement building is any temporary and/or permanent building or portion thereof that is occupied for amusement, entertainment, or educational purposes and that contains a device or system(s) that conveys passengers or provides a walkway along, around, or over a course in any direction so arranged that the means of egress path is not readily apparent due to visual or audio distractions or is intentionally confounded or is not readily available because of the nature of the attraction or mode of conveyance through the building or structure.

When an addition is attached to an existing building the entire building’s fire alarm system must meet the current requirements of the adopted International Building Code, International Fire Code, and the Life Safety Code 101 as it relates to the Fire Alarm System requirements. The activation of the Fire Alarm System shall stop any conflicting or confusing sounds and visual distractions upon the activation of the fire alarm system.

When a remodel to an existing building is being performed the entire building’s fire alarm system must meet the current requirements of the adopted International Building Code, International Fire Code, and the Life Safety Code 101 as it relates to the Fire Alarm System requirements. The activation of the Fire Alarm System shall stop any conflicting or confusing sounds and visual distractions upon the activation of the fire alarm system.

It is our hope that we can work together to develop new sites while remaining committed to maintaining the utmost level of life safety by making Oklahoma structures as safe as possible through congruent code enforcement.

Robert Doke

State Fire Marshal