Oklahoma State Fire Marshal’s Office

Official Interpretation and Code Directive 2013-8

Fire Alarm System Requirements for New Buildings and/or Additions to an

Existing Building without a Fire Hydrant within 1,000 feet of the Building

Effective June 1, 2013 (Revised 2-12-2018)

The guidelines set forth through the codes adopted by the Oklahoma Uniform Building Code Commission and enforced by the Oklahoma State Fire Marshals Office can help to establish the requirements for new and existing buildings without a fire hydrant within 1,000 feet of all sides of the building as the hose lays off the fire truck.  This directive is to help simplify and bring clarity as to what is required to be installed.

Any new building and/or addition to an Occupancy Classification identified in the International Building Code must adhere to the requirements to the adopted International Building Code (IBC) and International Fire Code (IFC).

When a new building and an addition is attached to an existing building a fire hydrant must be installed within 400 feet of a non-sprinklered building or 600 feet of a fully sprinklered building to the  new building and the new addition as per the adopted International Fire Code. When a properly sized (6”) water line to install a fire hydrant on is not located within 1,000 feet of the furthest point of the building being constructed an automatic fire detection system is required to be installed throughout.  When the fire hydrant requirement of the International Building Code cannot be met the options are as follows:  1) Extend the water line and install a fire hydrant as required by the International Fire Code, 2) Install smoke detection device in each room and install notification throughout as per International Building Code, International Fire Code, and National Fire Alarm and Signaling Code.  In addition the monitoring of the fire alarm system must be provided as per the International Building Code and International Fire Code.

We would require that a complete set of building plans identifying option 2 be submitted to our office for review of all buildings that fall within our jurisdiction including documentation which supports the decision.

It is our hope that we can work together to develop new sites while remaining committed to maintaining the utmost level of life safety by making Oklahoma structures as safe as possible through congruent code enforcement.

Robert Doke

State Fire Marshal