Office of the Oklahoma State Fire Marshal

PO Box 36690

Oklahoma City, OK 73136-2690

405-522-5005

www.ok.gov/fire/

Building Project Handbook

EACH SEPARATE BUILDING MUST BE PERMITTED SEPARATELY.

EACH SAFE ROOM/STORM SHELTER MUST BE PERMITTED SEPARATELY.  BUILDINGS WITH A SAFE ROOM/STORM SHELTER WITHIN A BUILDING MUST BE PERMITTED SEPARATELY.

A PHASED PROJECT MUST BE PERMITTED SEPARATELY.

A PROJECT WITH A REMODEL AND NEW CONSTRUCTION MUST BE PERMITTED SEPARATELY AND BE ACCOMPANIED BY A NEW BUILDING APPLICATION AND AN EXISTING BUILDING APPLICATION.

The Office of the Oklahoma State Fire Marshal is charged with the issuance of building permits in those areas of the state that do not require such permit.  In accordance with this statute, the OSFM requires the submission of plans and specifications to cover the proposed construction or alteration. (OS 74 § 324.11)

The OSFM shall review all plans and specification of proposed construction or alteration to any correctional facility as defined in OS 74 § 317. (OS 74 § 324.11)

Per OS 74 § 324.11, the following occupancies shall have a building permit issued by the OSFM when there is no local authority having jurisdiction;

All Occupancies Identified in the International Building Code

Projects that are exempt from the Architectural Act (refer to Title 59 O.S. § 46.1 et al) shall be drafted to a legible, professional standard suitable for review and possible permitting.

The minimum scale that drawings shall be drafted to is:

Architectural – 1/8” to 1 foot

Site Maps – 1” to 20’ or 30’ or 40’ feet (the best fit while showing sufficient detail)

All projects submitted to the OSFM shall be designed to those building codes and references as last adopted by the Uniform Building Code Commission, reference 59 O.S. § 1000.23.

REQUIRED DOCUMENTS

Completed permit application forms for each building in the project

NOTE:  Permit application forms must be completely filled out.

Completed checklist form for each building in the project

NOTE:  Checklist form must be completely filled out.

Two (2) paper sets of plans (as outlined below)

One (1) CD of the entire project plan, to include specs if applicable

Building project plans submitted to the OSFM for permitting shall consist of:

- A cover sheet detailing;

  - The name, location and owner(s) of the project (NOTE: The project name and address SHALL be on all submitted plans for other permitted construction such as fire alarm, sprinkler systems and alternative suppression systems)

  - The scope of work, to include;

    - List of codes and the applicable year that are applicable

    - Occupant load factor

    - Code defined use group(s)

    - Code define construction type(s)

    - Special use and occupancy requirements

    - Square footage of the project, to include all floors, roof overhangs, covered patios, decks, balconies, etc.

    - Identify and provide the square footage of all fire areas, when applicable

    - Number of stories

    - Elevator-hydraulic or electric (if applicable)

    - Allowable building heights and areas.  Designed building height and area

    - If allowable increases are taken, how the increases are made (must show calculations), or unlimited area building if permissible.

    - Roof assembly construction and rating

    - Occupant load-new and existing (if applicable)

    - Wall and ceiling finish classifications

    - Interior floor finish classification

    - Decorative materials and trim-the percentage allowed and the percentage that will be used

    - Fire sprinkler system required.   Fire sprinkler system present.  Fire sprinkler system being installed

    - Fire standpipe system required.  Fire standpipe system present.  Fire standpipe system being provided

    - Fire alarm system required.  Fire alarm system present.  Fire alarm system being installed

    - Carbon monoxide system required.  Carbon monoxide system present.  Carbon monoxide system being installed

    - Fire suppression system required.  Fire suppression system present.  Fire suppression system being installed

    - Smoke control system required.  Smoke control system present.  Smoke control system being installed

    - Smoke and Heat Vents required.  Smoke and/or heat vents present.  Smoke and/or heat vents being installed

    - Fire command center required.  Fire command center present.  Fire command center being installed.  Provide the proper rated enclosure

    - Fire pump required.  Fire pump present.  Fire pump being installed.  Provide the proper rated enclosure

    - Required plumbing fixtures and number of provided plumbing fixtures.  Provide the ratio

    - Reference modification to the IBC by the OUBCC

    - Codes utilized in the design (Must be the current adoption by the OUBCC, refer to http://www.ok.gov/oubcc/ or call 405-521-6501 for assistance)

  - Identify any specific chapters and/or sections of the International Fire Code as related to this project being used

  - If a remodel, what level of alteration per the IEBC.

    - Remodels are required to have known Code deficiencies identified and the proposed Code compliant corrections.

    - Building Layout:

- Dashed lines showing all walls being demolished

- Dashed lines showing all doors being demolished

- Details identifying the scope of work being done

- Identify any fire walls being affected

- Identify any fire barriers being affected

- Identify any fire partitions being affected

    - Remodels shall identify all systems (M, E, P, fire alarm, fire sprinkler, carbon monoxide, etc.) that will be effected and the extent of upgrades as defined by the IEBC.

    - Designers may request an OSFM inspection for deficiencies prior to submitting a project for review.

  - If an addition, the changes needed to the existing building for code compliance.

  - If an addition or remodel, what year was the current occupancy permitted (reference modification to the IEBC by the OUBCC)

  - Name, address and legal stamp of the designer (if required by Title 58 O.S. § 46.1 et al)

    - Wet or electronic stamps are accepted

    - Must be signed by the designer

  - Any alternatives that are selected.  Identify each alternate specifically

  - Any directives that are used.  Identify each directive applied

- Site map detailing

  - The physical location of the project and all structures within 30 feet of the project

    - Distances between buildings shall be dimensioned in feet

    - Means of egress locations shall be shown on all buildings within 30 feet of the project

  - The outline of the proposed project new and existing (if applicable)

  - Identify all lot lines indicating the private property side and public property side

  - Fire department access roads

    - Width at least 20’ wide

    - Length of road

    - Turn around (if required)

    - Provide a dimension of the distance from the roads to all sides of the building

    - Identify all designated fire department access lanes

  - All new fire hydrants must be installed within the Public Easement. A fire hydrant is required to be installed within 400’ of a non-sprinklered building and 600’ of a sprinklered building.  The new fire hydrants are measured as the hose lays off the back of the fire truck on a hard surface and not as the crow flies.

  - Identify all fire hydrants as either existing or new

- Project Plans

  - Another term for this is the “Life Safety Sheet”

  - The floor plan of the entire project, to include basements, crawlspaces and attics.

  - All rooms and spaces shall be named, or provided another designation, to permit easier identification in the review and inspections phases.

  - Occupant loads per room or space (table & chairs or other furniture may need to be drawn to establish a lower factor) along with the occupant load factor and square footage per room

  - Fuel Burning Appliance-Fuel Burning Fireplace-Fuel Burning Forced Air Furnace locations with ducting

  - All rated construction

    - Wall design and rating (fire wall, fire barrier, fire partition, draft stopping, load bearing walls), please utilize UL Fire Wizard (http://database.ul.com/cgi-bin/ulweb/LISEXT/1FRAME/FireResistanceWizard.html ) for assistance.  Identify the location of all fire walls, fire barriers, fire partitions, draft stopping, & load bearing walls.  Provide the associated hourly rating for each type of wall.  Provide the associated UL design cut sheet

    - Penetration protection (doors, dampers, piping, etc.) Identify the location of all dampers

    - Door and window design (occupant per door must be shown)  Identify the associated rating for each door and window.  Identify the location of all panic and fire exit hardware.  Identify the door swing.  Identify any special locking arrangements. Identify the location of all rescue windows

  - All elements of the means of egress

    - Maximum travel distance

    - Exit access

    - Egress path and travel distances

    - Exits (must show calculated occupant load egress along with the occupant load factor.  Identify any occupant load egress  as modified by the OUBCC)

      - If an alteration or addition, the calculated occupant load of the existing building must be included in the exit calculations.

      - All exits must be accurately shown for the existing building.

    - Exit discharge

    - Exit signs

    - Exit illumination (interior and exterior)

    - Rescue windows, if required. Windows designated for rescue shall have the dimensions shown of the opening.

    - Area(s) of refuge

    - Stairs and/or ramps

      - Pitch of stairs must be shown

      - Ramp incline must be shown

      - Handrail specifications

    - Corridor rating when applicable

    - Elevator and/or lift-electric or hydraulic

    - Specifically identify any dead-end corridors and calculated distances

  - Location of fire extinguishers with the associated travel distance

  - Fire command rooms specifically identified

  - Fire sprinkler riser room

  - Identify accessible dwelling and sleeping units (including hearing impaired rooms)

  - Identify accessible wheelchair  spaces where required

  - Provide a building section view elevation diagram with dimensions for multiple story buildings (more than 2 floors).

  - Provide a roof pitch for all buildings.

  - Identify all dead loads within 10’ of the roof edge and the location of all guards

- Safe Rooms/ Storm Shelters

  - All construction intended for this use shall be designed to the Codes and references as adopted or modified by OUBCC, regardless of the funding source.

  - All the above requirements shall be met, with the following additions:

    - All FEMA Tornado/Storm Shelter and safe room designs shall be accompanied by a completed 2015 edition, FEMA P-361 Appendix C form.

    - All ICC-500 Tornado/Storm Shelter and safe room designs shall be designed to ICC500.

    - All Tornado/Storm Shelters shall undergo a peer review prior to submittal to the OSFM.

      - The peer review report shall be attached to the submitted documents.

      - Any and all conflicts between the designer and peer review SHALL be resolved prior to submittal for review.

  - Fuel Burning Appliance-Fuel Burning Fireplace-Fuel Burning Forced Air Furnace locations with ducting

  - Planning and scheduling for the required special inspections and the quality assurance plan. Copies of these special inspection reports shall be presented to the OSFM Agent at the final inspection.

- Other permits

  - Some systems require additional permits.

    - Fire sprinkler

    - Alternative suppression (range hoods, paint booth, etc.)

    - Fire alarm

    - Carbon monoxide

    - Carbon dioxide

    - Access control

    - Smoke control

  - These are separate requirements, and must be submitted by a company licensed in Oklahoma to perform this work.

  - 50% inspections will not occur until all required permits are on site.

- Field inspections

  - All permitted projects are required to be inspected for compliance with the permit and the applicable codes.

  - Inspections are performed by OSFM Agents.

    - Promptness on the design or owner’s part can help reduce delays by making inspection requests on time.

  - Inspections occur at 50% and 100% stages of construction.

    - A 50% inspection requires the building to be weather-tight, and at least 1 (one) side of walls exposed to permit inspection.

      - 50% inspections will be coordinated with other permitted trades so that only 1 (one) site visit is necessary.

      - Agents are permitted to alter the 1 (one) 50% visit when they deem it necessary.

  - Agents may elect to perform an 80% inspection.

  - Agents perform a 100% inspection at the conclusion of the project.

    - The project shall be complete at the time of the 100% inspection.

    - All permitted aspects of the project must be completed at the time of the inspection.

      - There are tests which occur for systems (sprinkler, fire alarm, carbon monoxide, carbon dioxide, smoke control, access control,  etc.)

      - It is vitally important that all contractor tests be successfully completed prior to the 100% OSFM inspection.

    - Use of the 100% inspection to create “punch lists” will create additional costs and time delays.

  - Although the project is reviewed and permitted, it is not uncommon for Agents to identify issues that were unforeseen during the design and review processes.  Agent may issue order to be completed before the 100% inspection.

  - The Agent’s orders shall be completed before the 100% inspection for it to be successful.

  - Projects which fail at 100% shall be subject to re-inspection fees of $40.00 per hour, to include travel time.

  - To request an inspection please call the OSFM main number at (405) 522-5005.