STATE OF OKLAHOMA

OFFICE OF THE STATE FIRE MARSHAL

Carbon Dioxide Plan Review Submittal Requirements

The following is a list of requirements for all plan submittals. Any information that is not provided may result in the plans being rejected and returned without review.

Application

- Completed Application Form with all fields filled-in.

Plans

- Two (2) sets of (paper) plans showing all container locations, where it enters the building, piping, joints, and end use equipment.

- Plans must be original plans with carbon dioxide devices only

- Plans must be drawn and printed to a scale no smaller than 1/8”

- The carbon dioxide notification appliance cannot have the work “Fire” on the device

- Any activation of the carbon dioxide detector shall initiate a “Local Alarm” both audible and visual if a fire alarm system is not installed.

- Any activation of the carbon dioxide detector shall be tied to the fire alarm system and initiate the building’s fire alarm system if one is installed.

Specifications

- One (1) set of specification book/books.

- One (1) CD containing all drawings and specifications.

50% Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify wiring is strapped up

- Verify notification device back boxes are installed as per the reviewed plans

- Verify initiating device back boxes are installed as per the reviewed plans

Final Walkthrough

- One set of reviewed plans with the red stamps on it is required to be on site before the walkthrough.

- One set of reviewed submittal brochure with the red stamps on it is required to be on site before the walkthrough.

- Verify a record of completion is filled out prior to the test

- Verify all devices are installed as per the reviewed plans

- Verify all carbon dioxide detectors are at least 3’ from all diffusers

- Verify all carbon dioxide are at least 3’ from the tip of all ceiling fan blades

- Verify the breaker associated with the carbon dioxide system is labeled in red

- Verify the electrical panel and breaker is identified in/on the carbon dioxide device

- The carbon dioxide detector must be tested using carbon dioxide and introducing it into the sensing chamber or element

- The carbon dioxide notification appliance cannot have the work “Fire” on the device

- Any activation of the carbon dioxide detector shall initiate a “Local Alarm” both audible and visual if a fire alarm system is not installed.

- Any activation of the carbon dioxide detector shall be tied to the fire alarm system and initiate the building’s fire alarm system if one is installed.

- Verify a map showing the location of the carbon dioxide devices, power supply,

carbon dioxide tanks, carbon dioxide lines entering the building, and carbon dioxide joints in the lines