| LIQUID TIGHTNESS TESTS FOR SPILL BUCKETS AND CONTAINMENT SUMPS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| OKLAHOMA CORPORATION COMMISSION PETROLEUM STORAGE TANK DIVISION P.O. Box 52000 Oklahoma City, OK 73152-2000 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| REQUIRED ONCE EVERY THREE (3) YEARS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NOTE: THIS FORM MAY ALSO BE USED FOR NEW INSTALLATIONS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - FACILITY INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Facility ID: |  |  |  |  |  |  |  |  | Date of Test: / / |  |  |  |  |  |  |  |  |  |
| Facility Name: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Physical Address: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| City, State, & Zip: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - TESTING COMPANY INFORMATION |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Company Name: |  |  |  |  |  |  |  |  | Company Phone: |  |  |  |  |  |  |  |  |  |
| Tester Name & Certification No: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| - PROCEDURES AND INSTRUCTIONS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Component | Pass |  | Fail |  | Visual Fail |  | Repairs Made | Component |  |  |  |  | Pass | Fail | Visual Fail |  |  | Repairs Made |
| - CERTIFICATION (Read and sign after completing all sections) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| I certify under penalty of law that I have examined and am familiar with the information submitted on this form and believe that the information is true, accurate, and complete. Additionally, all liquid and debris used for testing have been disposed of properly. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| X |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Tester Signature |  |  |  |  |  |  |  |  | Date |  |  |  |  |  |  |  |  |  |
| - TESTING CONTAINMENT SUMPS |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Method Developed By: |  |  |  | Industry Standard Manufacturer |  |  |  |  |  | Other (specify below) |  |  |  |  |  |  |  |  |
| Test Method Used: |  |  |  | Hydrostatic Vacuum |  |  |  |  |  | Pressure Other (specify below) |  |  |  |  |  |  |  |  |
| Specify Here: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sump Number |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sump Material |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sump Diameter |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Sump Depth |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Height From Bottom to Highest Penetration or Sidewall Seam (inch) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Sump must pass visual inspection. Change in reading of less than 1/8 inch (0.125) |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS |  | Pass Fail |  |  |  | Pass Fail |  |  | Pass Fail |  | Pass Fail |  |  |  |  |  | Pass Fail |  |
| Was leak detection sensor properly replaced and verified as functional after testing? |  | Yes No n/a |  |  |  | Yes No n/a |  |  | Yes No n/a |  | Yes No n/a |  |  |  |  |  | Yes No n/a |  |
| Was the secondary piping boots opened after testing? |  | Yes No n/a |  |  |  | Yes No n/a |  |  | Yes No n/a |  | Yes No n/a |  |  |  |  |  | Yes No n/a |  |
| Comments: _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ ______________________________________________________________________________________________________________________________________________________________________________________________________ ___________________________________________________________________________________________________ |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

If additional sumps are tested, please make additional copies of this page.

| - TESTING UNDER DISPENSER CONTAINMENT (UDC) |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Method Developed By: |  | Industry Standard Manufacturer |  |  | Other (specify below) |  |  |  |  |
| Test Method Used: |  | Hydrostatic Vacuum |  |  | Pressure Other (specify below) |  |  |  |  |
| Specify Here: |  |  |  |  |  |  |  |  |  |
| Dispenser Number |  |  |  |  |  |  |  |  |  |
| UDC Manufacturer |  |  |  |  |  |  |  |  |  |
| UDC Depth |  |  |  |  |  |  |  |  |  |
| Height From Bottom to Highest Penetration or Sidewall Seam (inch) |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Sump must pass visual inspection. Change in reading of less than 1/8 inch (0.125) |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail |  |  | Pass Fail |
| Was leak detection sensor properly replaced and verified as functional after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Was the secondary piping boots opened after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Dispenser Number |  |  |  |  |  |  |  |  |  |
| UDC Manufacturer |  |  |  |  |  |  |  |  |  |
| UDC Depth |  |  |  |  |  |  |  |  |  |
| Height From Bottom to Highest Penetration or Sidewall Seam (inch) |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Sump must pass visual inspection. Change in reading of less than 1/8 inch (0.125) |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail |  |  | Pass Fail |
| Was leak detection sensor properly replaced and verified as functional after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Was the secondary piping boots opened after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| - TESTING UNDER DISPENSER CONTAINMENT (UDC) – CONTINUED |  |  |  |  |  |  |  |  |  |
| Dispenser Number |  |  |  |  |  |  |  |  |  |
| UDC Manufacturer |  |  |  |  |  |  |  |  |  |
| UDC Depth |  |  |  |  |  |  |  |  |  |
| Height From Bottom to Highest Penetration or Sidewall Seam (inch) |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Sump must pass visual inspection. Change in reading of less than 1/8 inch (0.125) |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail |  |  | Pass Fail |
| Was leak detection sensor properly replaced and verified as functional after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Was the secondary piping boots opened after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Dispenser Number |  |  |  |  |  |  |  |  |  |
| UDC Manufacturer |  |  |  |  |  |  |  |  |  |
| UDC Depth |  |  |  |  |  |  |  |  |  |
| Height From Bottom to Highest Penetration or Sidewall Seam (inch) |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Sump must pass visual inspection. Change in reading of less than 1/8 inch (0.125) |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail |  |  | Pass Fail |
| Was leak detection sensor properly replaced and verified as functional after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Was the secondary piping boots opened after testing? | Yes No n/a |  | Yes No n/a | Yes No n/a |  | Yes No n/a |  |  | Yes No n/a |
| Comments: _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ |  |  |  |  |  |  |  |  |  |
| - TESTING SPILL BUCKETS |  |  |  |  |  |  |  |  |  |
| Test Method Developed By: |  | Industry Standard Manufacturer |  |  | Other (specify below) |  |  |  |  |
| Specify Here: |  |  |  |  |  |  |  |  |  |
| Tank Number |  |  |  |  |  |  |  |  |  |
| Bucket Construction | Single-walled Double-walled |  | Single-walled Double-walled | Single-walled Double-walled |  |  | Single-walled Double-walled | Single-walled Double-walled |  |
| Test Type | Hydrostatic Vacuum |  | Hydrostatic Vacuum | Hydrostatic Vacuum |  |  | Hydrostatic Vacuum | Hydrostatic Vacuum |  |
| Bucket Diameter |  |  |  |  |  |  |  |  |  |
| Bucket Depth |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Spill bucket must pass visual inspection. Hydrostatic: water level drop of less than 1/8 inch (0.125); Vacuum (single walled): maintain at least 26 inches water column; Vacuum (double walled): maintain at least 12 inches water column. |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail |  |  | Pass Fail |
| Tank Number |  |  |  |  |  |  |  |  |  |
| Bucket Construction | Single-walled Double-walled |  | Single-walled Double-walled | Single-walled Double-walled |  |  | Single-walled Double-walled | Single-walled Double-walled |  |
| Test Type | Hydrostatic Vacuum |  | Hydrostatic Vacuum | Hydrostatic Vacuum |  |  | Hydrostatic Vacuum | Hydrostatic Vacuum |  |
| Bucket Diameter |  |  |  |  |  |  |  |  |  |
| Bucket Depth |  |  |  |  |  |  |  |  |  |
| Test Start Time |  |  |  |  |  |  |  |  |  |
| Initial Reading (R1) |  |  |  |  |  |  |  |  |  |
| Test End Time |  |  |  |  |  |  |  |  |  |
| Final Reading (R2) |  |  |  |  |  |  |  |  |  |
| Change In Reading (R1 – R2) |  |  |  |  |  |  |  |  |  |
| Pass/Fail criteria: Spill bucket must pass visual inspection. Hydrostatic: water level drop of less than 1/8 inch (0.125); Vacuum (single walled): maintain at least 26 inches water column; Vacuum (double walled): maintain at least 12 inches water column. |  |  |  |  |  |  |  |  |  |
| FINAL TEST RESULTS | Pass Fail |  | Pass Fail | Pass Fail |  | Pass Fail |  |  | Pass Fail |
| Comments: _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ _____________________________________________________________________________________________________________ |  |  |  |  |  |  |  |  |  |

KEEP THIS RECORD FOR THREE (3) YEARS.